## Sayfa1
index | enable | slave | interval | sort_index | fcode | length | byte_format | tagname | type | register
0 | true | 11 | 1 | 1 | 4 | 1 | AB | Invertor_11_Yields_DailyPower | UINT | 5002
0 | true | 11 | 1 | 2 | 4 | 2 | CDAB | Invertor_11_Yields_TotalPower | UDINT | 5003
0 | true | 11 | 1 | 3 | 4 | 2 | CDAB | Invertor_11_Time_TotalRunningTime | UDINT | 5005
0 | true | 11 | 1 | 4 | 4 | 1 | AB | Invertor_11_Temp_InternalTemp | INT | 5007
0 | true | 11 | 1 | 5 | 4 | 2 | CDAB | Invertor_11_Power_TotalApparent | UDINT | 5008
0 | true | 11 | 1 | 6 | 4 | 1 | AB | Invertor_11_Voltage_MPPT1 | UINT | 5010
0 | true | 11 | 1 | 7 | 4 | 1 | AB | Invertor_11_Current_MPPT1 | UINT | 5011
0 | true | 11 | 1 | 8 | 4 | 2 | CDAB | Invertor_11_Power_TotalDC | UDINT | 5016
0 | true | 11 | 1 | 9 | 4 | 1 | AB | Invertor_11_Voltage_APhase | UINT | 5018
0 | true | 11 | 1 | 10 | 4 | 1 | AB | Invertor_11_Voltage_BPhase | UINT | 5019
0 | true | 11 | 1 | 11 | 4 | 1 | AB | Invertor_11_Voltage_CPhase | UINT | 5020
0 | true | 11 | 1 | 12 | 4 | 1 | AB | Invertor_11_Current_APhase | UINT | 5021
0 | true | 11 | 1 | 13 | 4 | 1 | AB | Invertor_11_Current_BPhase | UINT | 5022
0 | true | 11 | 1 | 14 | 4 | 1 | AB | Invertor_11_Current_CPhase | UINT | 5023
0 | true | 11 | 1 | 15 | 4 | 2 | CDAB | Invertor_11_Power_TotalActive | UDINT | 5030
0 | true | 11 | 1 | 16 | 4 | 2 | CDAB | Invertor_11_Power_TotalReactive | DINT | 5032
0 | true | 11 | 1 | 17 | 4 | 1 | AB | Invertor_11_Power_Factor | INT | 5034
0 | true | 11 | 1 | 18 | 4 | 1 | AB | Invertor_11_Frequency_Grid | UINT | 5035
0 | true | 11 | 1 | 19 | 4 | 1 | AB | Invertor_11_State_Work | UINT | 5037
0 | true | 11 | 1 | 20 | 4 | 1 | AB | Invertor_11_Fault_TimeYear | UINT | 5038
0 | true | 11 | 1 | 21 | 4 | 1 | AB | Invertor_11_Fault_TimeMonth | UINT | 5039
0 | true | 11 | 1 | 22 | 4 | 1 | AB | Invertor_11_Fault_TimeDay | UINT | 5040
0 | true | 11 | 1 | 23 | 4 | 1 | AB | Invertor_11_Fault_TimeHour | UINT | 5041
0 | true | 11 | 1 | 24 | 4 | 1 | AB | Invertor_11_Fault_TimeMinute | UINT | 5042
0 | true | 11 | 1 | 25 | 4 | 1 | AB | Invertor_11_Fault_TimeSecond | UINT | 5043
0 | true | 11 | 1 | 26 | 4 | 1 | AB | Invertor_11_Fault_Code | UINT | 5044
0 | true | 11 | 1 | 27 | 4 | 1 | AB | Invertor_11_Power_NomReactive | UINT | 5048
0 | true | 11 | 1 | 28 | 4 | 2 | CDAB | Invertor_11_State_Work2 | UDINT | 5080
0 | true | 11 | 1 | 29 | 4 | 1 | AB | Invertor_11_Time_DailyRun | UINT | 5112
0 | true | 11 | 1 | 30 | 4 | 1 | AB | Invertor_11_Country_Present | UINT | 5113
0 | true | 11 | 1 | 31 | 4 | 2 | CDAB | Invertor_11_Yields_MonthlyPower | UDINT | 5127
0 | true | 11 | 1 | 32 | 4 | 1 | AB | Invertor_11_Voltage_NegativeToGround | INT | 5145
0 | true | 11 | 1 | 33 | 4 | 1 | AB | Invertor_11_Voltage_Bus | UINT | 5146
0 | true | 11 | 1 | 34 | 4 | 1 | AB | Invertor_11_Frequency_Grid2 | UINT | 5147
0 | true | 11 | 1 | 35 | 4 | 1 | AB | Invertor_11_Current_1String | UINT | 7012
0 | true | 11 | 1 | 36 | 4 | 1 | AB | Invertor_11_Current_2String | UINT | 7013
0 | true | 11 | 1 | 37 | 4 | 1 | AB | Invertor_11_Current_3String | UINT | 7014
0 | true | 11 | 1 | 38 | 4 | 1 | AB | Invertor_11_Current_4String | UINT | 7015
0 | true | 11 | 1 | 39 | 4 | 1 | AB | Invertor_11_Current_5String | UINT | 7016
0 | true | 11 | 1 | 40 | 4 | 1 | AB | Invertor_11_Current_6String | UINT | 7017
0 | true | 11 | 1 | 41 | 4 | 1 | AB | Invertor_11_Current_7String | UINT | 7018
0 | true | 11 | 1 | 42 | 4 | 1 | AB | Invertor_11_Current_8String | UINT | 7019
0 | true | 11 | 1 | 43 | 4 | 1 | AB | Invertor_11_Current_9String | UINT | 7020
0 | true | 11 | 1 | 44 | 4 | 1 | AB | Invertor_11_Current_10String | UINT | 7021
0 | true | 11 | 1 | 45 | 4 | 1 | AB | Invertor_11_Current_11String | UINT | 7022
0 | true | 11 | 1 | 46 | 4 | 1 | AB | Invertor_11_Current_12String | UINT | 7023
0 | true | 11 | 1 | 47 | 4 | 1 | AB | Invertor_11_Switch_StartStop | UINT | 5005
0 | true | 11 | 1 | 48 | 4 | 1 | AB | Invertor_11_Switch_PowerLimit | UINT | 5006
0 | true | 11 | 1 | 49 | 4 | 1 | AB | Invertor_11_Setting_PowerLimit | UINT | 5007

## Sayfa2
Site number | Device | Parameter Name | Classification Name | MB Adress | Data Type and Func | Device ID | Idx-1 | Coefficient and UNIT | Coefficient - Dividing Operant | DATA TYPE | MB Tags | MB Tags New Style | MQTT Telemetry Tag Name | MQTT Buffer Telemetry Alias Name (Site) | MQTT Buffer Telemetry Alias Name (CAP)
TR-68 | Invertor | DailyPower | Yields | 5003 | U16x04 | 11 | Yes | 0.1 kWh | 10 | UINT | DailyPowerYields_5003_U16x04_11 | Invertor_11_Yields_DailyPower | TELEMETRY_P_Invertor_11_Yields_DailyPower | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Yields_DailyPower | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Yields_DailyPower
TR-68 | Invertor | TotalPower | Yields | 5004 | U32x04 | 11 | Yes | kWh | 1 | UDINT | TotalPowerYields_5004_U32x04_11 | Invertor_11_Yields_TotalPower | TELEMETRY_P_Invertor_11_Yields_TotalPower | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Yields_TotalPower | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Yields_TotalPower
TR-68 | Invertor | TotalRunningTime | Time | 5006 | U32x04 | 11 | Yes | h | 1 | UDINT | TotalRunningTime_5006_U32x04_11 | Invertor_11_Time_TotalRunningTime | TELEMETRY_P_Invertor_11_Time_TotalRunningTime | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Time_TotalRunningTime | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Time_TotalRunningTime
TR-68 | Invertor | InternalTemp | Temp | 5008 | S16x04 | 11 | Yes | 0.1℃ | 10 | INT | InternalTemp_5008_S16x04_11 | Invertor_11_Temp_InternalTemp | TELEMETRY_P_Invertor_11_Temp_InternalTemp | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Temp_InternalTemp | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Temp_InternalTemp
TR-68 | Invertor | TotalApparent | Power | 5009 | U32x04 | 11 | Yes | VA | 1 | UDINT | TotalApparentP_5009_U32x04_11 | Invertor_11_Power_TotalApparent | TELEMETRY_P_Invertor_11_Power_TotalApparent | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Power_TotalApparent | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Power_TotalApparent
TR-68 | Invertor | MPPT1 | Voltage | 5011 | U16x04 | 11 | Yes | 0.1V | 10 | UINT | MPPT1Voltage_5011_U16x04_11 | Invertor_11_Voltage_MPPT1 | TELEMETRY_P_Invertor_11_Voltage_MPPT1 | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Voltage_MPPT1 | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Voltage_MPPT1
TR-68 | Invertor | MPPT1 | Current | 5012 | U16x04 | 11 | Yes | 0.1A | 10 | UINT | MPPT1Current_5012_U16x04_11 | Invertor_11_Current_MPPT1 | TELEMETRY_P_Invertor_11_Current_MPPT1 | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_MPPT1 | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_MPPT1
TR-68 | Invertor | TotalDC | Power | 5017 | U32x04 | 11 | Yes | W | 1 | UDINT | TotalDCPower_5017_U32x04_11 | Invertor_11_Power_TotalDC | TELEMETRY_P_Invertor_11_Power_TotalDC | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Power_TotalDC | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Power_TotalDC
TR-68 | Invertor | APhase | Voltage | 5019 | U16x04 | 11 | Yes | 0.1 V | 10 | UINT | PhaseAvoltage_5019_U16x04_11 | Invertor_11_Voltage_APhase | TELEMETRY_P_Invertor_11_Voltage_APhase | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Voltage_APhase | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Voltage_APhase
TR-68 | Invertor | BPhase | Voltage | 5020 | U16x04 | 11 | Yes | 0.1 V | 10 | UINT | PhaseBvoltage_5020_U16x04_11 | Invertor_11_Voltage_BPhase | TELEMETRY_P_Invertor_11_Voltage_BPhase | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Voltage_BPhase | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Voltage_BPhase
TR-68 | Invertor | CPhase | Voltage | 5021 | U16x04 | 11 | Yes | 0.1 V | 10 | UINT | PhaseCvoltage_5021_U16x04_11 | Invertor_11_Voltage_CPhase | TELEMETRY_P_Invertor_11_Voltage_CPhase | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Voltage_CPhase | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Voltage_CPhase
TR-68 | Invertor | APhase | Current | 5022 | U16x04 | 11 | Yes | 0.1 A | 10 | UINT | PhaseACurrent_5022_U16x04_11 | Invertor_11_Current_APhase | TELEMETRY_P_Invertor_11_Current_APhase | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_APhase | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_APhase
TR-68 | Invertor | BPhase | Current | 5023 | U16x04 | 11 | Yes | 0.1 A | 10 | UINT | PhaseBCurrent_5023_U16x04_11 | Invertor_11_Current_BPhase | TELEMETRY_P_Invertor_11_Current_BPhase | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_BPhase | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_BPhase
TR-68 | Invertor | CPhase | Current | 5024 | U16x04 | 11 | Yes | 0.1 A | 10 | UINT | PhaseCCurrent_5024_U16x04_11 | Invertor_11_Current_CPhase | TELEMETRY_P_Invertor_11_Current_CPhase | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_CPhase | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_CPhase
TR-68 | Invertor | TotalActive | Power | 5031 | U32x04 | 11 | Yes | W | 1 | UDINT | TotalActivePower_5031_U32x04_11 | Invertor_11_Power_TotalActive | TELEMETRY_P_Invertor_11_Power_TotalActive | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Power_TotalActive | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Power_TotalActive
TR-68 | Invertor | TotalReactive | Power | 5033 | S32x04 | 11 | Yes | Var | 1 | DINT | TotalReactivePwr_5033_S32x04_11 | Invertor_11_Power_TotalReactive | TELEMETRY_P_Invertor_11_Power_TotalReactive | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Power_TotalReactive | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Power_TotalReactive
TR-68 | Invertor | Factor | Power | 5035 | S16x04 | 11 | Yes | 0.001 | 1000 | INT | PowerFactor_5035_S16x04_11 | Invertor_11_Power_Factor | TELEMETRY_P_Invertor_11_Power_Factor | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Power_Factor | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Power_Factor
TR-68 | Invertor | Grid | Frequency | 5036 | U16x04 | 11 | Yes | 0.1 Hz | 10 | UINT | GridFrequency_5036_U16x04_11 | Invertor_11_Frequency_Grid | TELEMETRY_P_Invertor_11_Frequency_Grid | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Frequency_Grid | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Frequency_Grid
TR-68 | Invertor | Work | State | 5038 | U16x04 | 11 | Yes |  | 1 | UINT | WorkState_5038_U16x04_11 | Invertor_11_State_Work | TELEMETRY_P_Invertor_11_State_Work | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_State_Work | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_State_Work
TR-68 | Invertor | TimeYear | Fault | 5039 | U16x04 | 11 | Yes |  | 1 | UINT | FaultTimeYear_5039_U16x04_11 | Invertor_11_Fault_TimeYear | TELEMETRY_P_Invertor_11_Fault_TimeYear | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Fault_TimeYear | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Fault_TimeYear
TR-68 | Invertor | TimeMonth | Fault | 5040 | U16x04 | 11 | Yes |  | 1 | UINT | FaultTimeMonth_5040_U16x04_11 | Invertor_11_Fault_TimeMonth | TELEMETRY_P_Invertor_11_Fault_TimeMonth | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Fault_TimeMonth | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Fault_TimeMonth
TR-68 | Invertor | TimeDay | Fault | 5041 | U16x04 | 11 | Yes |  | 1 | UINT | FaultTimeDay_5041_U16x04_11 | Invertor_11_Fault_TimeDay | TELEMETRY_P_Invertor_11_Fault_TimeDay | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Fault_TimeDay | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Fault_TimeDay
TR-68 | Invertor | TimeHour | Fault | 5042 | U16x04 | 11 | Yes |  | 1 | UINT | FaultTimeHour_5042_U16x04_11 | Invertor_11_Fault_TimeHour | TELEMETRY_P_Invertor_11_Fault_TimeHour | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Fault_TimeHour | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Fault_TimeHour
TR-68 | Invertor | TimeMinute | Fault | 5043 | U16x04 | 11 | Yes |  | 1 | UINT | FaultTimeMinute_5043_U16x04_11 | Invertor_11_Fault_TimeMinute | TELEMETRY_P_Invertor_11_Fault_TimeMinute | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Fault_TimeMinute | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Fault_TimeMinute
TR-68 | Invertor | TimeSecond | Fault | 5044 | U16x04 | 11 | Yes |  | 1 | UINT | FaultTimeSecond_5044_U16x04_11 | Invertor_11_Fault_TimeSecond | TELEMETRY_P_Invertor_11_Fault_TimeSecond | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Fault_TimeSecond | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Fault_TimeSecond
TR-68 | Invertor | Code | Fault | 5045 | U16x04 | 11 | Yes |  | 1 | UINT | FaultCode1_5045_U16x04_11 | Invertor_11_Fault_Code | TELEMETRY_P_Invertor_11_Fault_Code | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Fault_Code | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Fault_Code
TR-68 | Invertor | NomReactive | Power | 5049 | U16x04 | 11 | Yes | 0.1kVar | 10 | UINT | NomReactivePower_5049_U16x04_11 | Invertor_11_Power_NomReactive | TELEMETRY_P_Invertor_11_Power_NomReactive | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Power_NomReactive | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Power_NomReactive
TR-68 | Invertor | Work2 | State | 5081 | U32x04 | 11 | Yes |  | 1 | UDINT | WorkState_5081_U32x04_11 | Invertor_11_State_Work2 | TELEMETRY_P_Invertor_11_State_Work2 | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_State_Work2 | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_State_Work2
TR-68 | Invertor | DailyRun | Time | 5113 | U16x04 | 11 | Yes | 1min | 1 | UINT | DailyRunTime_5113_U16x04_11 | Invertor_11_Time_DailyRun | TELEMETRY_P_Invertor_11_Time_DailyRun | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Time_DailyRun | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Time_DailyRun
TR-68 | Invertor | Present | Country | 5114 | U16x04 | 11 | Yes |  | 1 | UINT | PresentCountry_5114_U16x04_11 | Invertor_11_Country_Present | TELEMETRY_P_Invertor_11_Country_Present | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Country_Present | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Country_Present
TR-68 | Invertor | MonthlyPower | Yields | 5128 | U32x04 | 11 | Yes |  | 1 | UDINT | MonthlyPwrYields_5128_U32x04_11 | Invertor_11_Yields_MonthlyPower | TELEMETRY_P_Invertor_11_Yields_MonthlyPower | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Yields_MonthlyPower | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Yields_MonthlyPower
TR-68 | Invertor | NegativeToGround | Voltage | 5146 | S16x04 | 11 | Yes | 0.1V | 10 | INT | NegativeVToGround_5146_S16x04_11 | Invertor_11_Voltage_NegativeToGround | TELEMETRY_P_Invertor_11_Voltage_NegativeToGround | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Voltage_NegativeToGround | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Voltage_NegativeToGround
TR-68 | Invertor | Bus | Voltage | 5147 | U16x04 | 11 | Yes | 0.1V | 10 | UINT | BusVoltage_5147_U16x04_11 | Invertor_11_Voltage_Bus | TELEMETRY_P_Invertor_11_Voltage_Bus | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Voltage_Bus | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Voltage_Bus
TR-68 | Invertor | Grid2 | Frequency | 5148 | U16x04 | 11 | Yes | 0.01Hz | 100 | UINT | GridFrequency_5148_U16x04_11 | Invertor_11_Frequency_Grid2 | TELEMETRY_P_Invertor_11_Frequency_Grid2 | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Frequency_Grid2 | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Frequency_Grid2
TR-68 | Invertor | 1String | Current | 7013 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String1Current_7013_U16x04_11 | Invertor_11_Current_1String | TELEMETRY_P_Invertor_11_Current_1String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_1String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_1String
TR-68 | Invertor | 2String | Current | 7014 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String2Current_7014_U16x04_11 | Invertor_11_Current_2String | TELEMETRY_P_Invertor_11_Current_2String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_2String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_2String
TR-68 | Invertor | 3String | Current | 7015 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String3Current_7015_U16x04_11 | Invertor_11_Current_3String | TELEMETRY_P_Invertor_11_Current_3String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_3String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_3String
TR-68 | Invertor | 4String | Current | 7016 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String4Current_7016_U16x04_11 | Invertor_11_Current_4String | TELEMETRY_P_Invertor_11_Current_4String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_4String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_4String
TR-68 | Invertor | 5String | Current | 7017 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String5Current_7017_U16x04_11 | Invertor_11_Current_5String | TELEMETRY_P_Invertor_11_Current_5String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_5String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_5String
TR-68 | Invertor | 6String | Current | 7018 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String6Current_7018_U16x04_11 | Invertor_11_Current_6String | TELEMETRY_P_Invertor_11_Current_6String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_6String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_6String
TR-68 | Invertor | 7String | Current | 7019 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String7Current_7019_U16x04_11 | Invertor_11_Current_7String | TELEMETRY_P_Invertor_11_Current_7String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_7String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_7String
TR-68 | Invertor | 8String | Current | 7020 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String8Current_7020_U16x04_11 | Invertor_11_Current_8String | TELEMETRY_P_Invertor_11_Current_8String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_8String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_8String
TR-68 | Invertor | 9String | Current | 7021 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String9Current_7021_U16x04_11 | Invertor_11_Current_9String | TELEMETRY_P_Invertor_11_Current_9String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_9String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_9String
TR-68 | Invertor | 10String | Current | 7022 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String10Current_7022_U16x04_11 | Invertor_11_Current_10String | TELEMETRY_P_Invertor_11_Current_10String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_10String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_10String
TR-68 | Invertor | 11String | Current | 7023 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String11Current_7023_U16x04_11 | Invertor_11_Current_11String | TELEMETRY_P_Invertor_11_Current_11String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_11String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_11String
TR-68 | Invertor | 12String | Current | 7024 | U16x04 | 11 | Yes | 0.01A | 100 | UINT | String12Current_7024_U16x04_11 | Invertor_11_Current_12String | TELEMETRY_P_Invertor_11_Current_12String | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Current_12String | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Current_12String
TR-68 | Invertor | StartStop | Switch | 5006 | U16x03 | 11 | Yes |  | 1 | UINT | StartStop_5006_U16x03_11 | Invertor_11_Switch_StartStop | TELEMETRY_P_Invertor_11_Switch_StartStop | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Switch_StartStop | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Switch_StartStop
TR-68 | Invertor | PowerLimit | Switch | 5007 | U16x03 | 11 | Yes |  | 1 | UINT | PowerLimitSwitch_5007_U16x03_11 | Invertor_11_Switch_PowerLimit | TELEMETRY_P_Invertor_11_Switch_PowerLimit | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Switch_PowerLimit | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Switch_PowerLimit
TR-68 | Invertor | PowerLimit | Setting | 5008 | U16x03 | 11 | Yes | 0.001 | 100 | UINT | PowerLimitSetting_5008_U16x03_11 | Invertor_11_Setting_PowerLimit | TELEMETRY_P_Invertor_11_Setting_PowerLimit | TR.CONSUMERS.TR-68 Vaener Aysebaci.Balikesir.SITE.Invertor_11_Setting_PowerLimit | TR.CONSUMERS.TR-68.Vaener.Solar.Balikesir.CAP1.Invertor_11_Setting_PowerLimit
DATA TYPE | FORMAT
REAL | ABCD
UDINT | CDAB
DINT | CDAB
INT | AB
UINT | AB